## Sheet1
کیا تهویه آراد
44482544-22515912
KIA General Data - Floor Standing Concealed FCU
KTAFR |  | 200D | 300D | 400D | 500D | 600D | 800D | 1000D | 1200D | 1400D
Air Flow m³/h | High | 350 | 520 | 680 | 850 | 1030 | 1380 | 1710 | 2040 | 2400
| Medium | 270 | 380 | 510 | 640 | 780 | 1030 | 1290 | 1540 | 1975
| Low | 190 | 280 | 340 | 450 | 560 | 740 | 890 | 1040 | 1255
Total Cooling Capacity W | High | 1970 | 2850 | 3760 | 4600 | 5450 | 7310 | 9000 | 10800 | 13000
| Medium | 1780 | 2480 | 3250 | 3860 | 4600 | 6215 | 7920 | 9400 | 11700
| Low | 1460 | 2050 | 2655 | 3030 | 4000 | 5190 | 6120 | 7230 | 7560
Sensible Cooling Capacity W | High | 1417 | 2050 | 2713 | 3307 | 3920 | 5260 | 6480 | 7760 | 9360
| Medium | 1255 | 1720 | 2270 | 2700 | 3330 | 4365 | 5570 | 6520 | 7950
| Low | 935 | 1390 | 1830 | 2050 | 2700 | 3520 | 4150 | 4780 | 5710
Heating Capacity W | High | 3480 | 5350 | 6700 | 7800 | 9000 | 11800 | 13880 | 16700 | 20040
Fan | Type | Centrifugal(Blade:Forward-Curved)
| Quantity | 1 | 2 | 2 | 2 | 2 | 3 | 4 | 4 | 4
Motor | Type | Split-capacitor motor with ball bearing
| Insulation Class | B
| Power Supply | 220V~50Hz
| Quantity | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
High Rated Power Input (3 rows coil)W | S | 30 | 45 | 55 | 75 | 90 | 128 | 150 | 189 | 228
| 30Pa | 42 | 55 | 65 | 82 | 105 | 148 | 171 | 212 | 253
| 50Pa | 47 | 62 | 75 | 91 | 115 | 165 | 203 | 250 | 290
Coil | Type | Seamless copper tube mechanically bonded to aluminum hydrophilic fin
| Max. Working Pressure Mpa | 1.6
| Pipe Connection | Rc3/4(Taper Pipe Female Threaded)
| Water Flow Rate m³/h | 0.34 | 0.49 | 0.65 | 0.79 | 0.94 | 1.25 | 1.55 | 1.85 | 2.23
| Water Pressure Drop kPa | 3.4 | 7.6 | 13 | 21 | 31.2 | 10 | 15.7 | 22.8 | 38
Dimension | Length mm | 640 | 760 | 880 | 1000 | 1120 | 1505 | 1625 | 1745 | 1870
| Width mm | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 255
| Height mm | 620 | 620 | 620 | 620 | 620 | 620 | 620 | 620 | 680
Weight kg |  | 18 | 22 | 24 | 30 | 36 | 52 | 58 | 64 | 75
High Sound Pressure Level | S(12Pa) | 36.5 | 38 | 40.5 | 42 | 45 | 46 | 47.5 | 49 | 51
| 30Pa | 39 | 41 | 43 | 44 | 46 | 47 | 49 | 51 | 52
| 50Pa | 42 | 43 | 45 | 47 | 49 | 50 | 52 | 53 | 53
Condensate Drain Size |  | R 3/4(Taper Pipe Male Threaded)
Note:
1. Cooling capacity is based on the following:
a) Water temperature : 7°C (inlet)/12°C (outlet)
b) Air entering condition : 27°C DB/19.5°C WB
2. Heating capacity is based on the following (with same water flow rate as cooling cycle):
a) Water temperature : 60°C (inlet)
b) Air entering condition : 21°C DB
3. Low ESP means 0Pa with air vent & filter and 12Pa without air vent& filter.
4. The air volume is tested under entering air condtion of 20°C DB and dry coil condition.
5. The sound pressure level is based on 11.5dB(A) hemi-anechoic room background noise.
6. The manufacturer reserves the rights to make changes to the above specifications without prior notice.