## Sheet1
کیا تهویه آراد
44482544-22515912
KTACRQ Celling Concealed Low Noise FCU (With separate heating coil,3+1)
Model KTACRQ |  | 400B | 500B | 600B | 800B
Air Flow m³/h | High | 680 | 850 | 1020 | 1360
| Medium | 510 | 640 | 780 | 1030
| Low | 340 | 450 | 560 | 740
Total Cooling Capacity W | High | 4020 | 4850 | 6010 | 7950
| Medium | 3350 | 4200 | 5280 | 6735
| Low | 2445 | 3270 | 4105 | 5260
Sensible Cooling Capacity W | High | 2830 | 3400 | 4180 | 5590
| Medium | 2300 | 2900 | 3610 | 4660
| Low | 1655 | 2200 | 2750 | 3560
Heating Capacity W | High | 4090 | 4800 | 5690 | 7700
Fan | Type | Centrifugal(Blade:Forward-Curved)
| Quantity | 2 | 2 | 2 | 3
Motor | Type | Split-capacitor motor with ball bearing
| Insulation Class | B
| Power Supply | 220v/1~/50Hz
| Quantity | 1 | 1 | 1 | 2
(High) Rated Power Input W | 12Pa | 49 | 75 | 92 | 115
| 30Pa | 72 | 87 | 107 | 155
Coil | Type | Seamless copper tube mechanically bonded to aluminum hydrophilic fin
| Max. Working Pressure Mpa | 1.6
| Pipe Connection | Rc3/4(Taper Pipe Female Threaded)
Water Flow Rate m³/h | Cooling Coil | 0.74 | 0.87 | 1.07 | 1.41
| Heating Coil | 0.31 | 0.42 | 0.49 | 0.66
Water Pressure Drop kPa | Cooling Coil | 30 | 30 | 40 | 40
| Heating Coil | 30 | 30 | 20 | 30
Weight (Without return air plenum) kg |  | 18.5 | 19.5 | 23 | 29
Dimension (Without return air plenum ) | Length mm | 925 | 1005 | 1205 | 1485
| Width mm | 490 | 490 | 515 | 515
| Height mm | 250 | 250 | 275 | 275
Sound Pressure Level dB(A) | 12Pa(H) | 38 | 41 | 43 | 43
| 12Pa(M) | 33 | 34 | 38.5 | 39
| 12Pa(L) | 25 | 27 | 31 | 30
| 30Pa(H) | 41.5 | 43 | 44.5 | 46
| 30Pa(M) | 35 | 36 | 39.5 | 40
| 30Pa(L) | 27 | 29 | 32 | 31
Condensate Drain Size |  | R 3/4(Taper Pipe Male Threaded)
Note:
1. Cooling capacity is based on the following:
a) Water temperature : 7°C (inlet)/12°C (outlet)
b) Air entering condition : 27°C DB/19.5°C WB
2. Heating capacity is based on the following:
a) Water temperature : 60°C (inlet)/50°C (outlet)
b) Air entering condition : 21°C DB
3. Low ESP means 0Pa with air vent & filter and 12Pa without air vent& filter.
4. The air volume is tested under entering air condtion of 20°C DB，15°CWB and dry coil condition.
5. The sound pressure level is based on 11.5dB(A) hemi-anechoic room background noise.
6. Cooling coils: 3 rows, heating coils: 1 rows
7. The manufacturer reserves the rights to make changes to the above specifications without prior notice.